Atrium Siphonic drainage calculations

A=1062m2

H=21.5m

From Brief specified by the client, a design rainfall intensity of 0.02l/s/m2

1.3(climate factor) x 0.02 x 1.1 (safety factor) x 1062 (area) = 31.64l/s/m2

Q1=Q2 = 31.64/2 = 15.82l/s

Q3=31.64l/s

1st Iteration using Cole-Brooke white formula
(u28gdi)logkp3710di+1.775v(gifdi3)-2

Q1 = 0.01582m3/s

V1 = 10.4m/s

------------------------------------------------------------------------------------------------------------------------

P1:  d1 = 44mm     X-SA = 0.001521m2      L1 = 8.4m    Q1 = 0.01582m3/s    V1 = 10.4m/s

P2:  “

P3:  d3 = 44mm     X-SA = 0.001521m2      L2 = 15.2m  Q1 = 0.01582m3/s    V3 = 10.4m/s

P4: d4 = 62mm      X-SA = 0.003042m2      L4 = 13.1m   Q4 = 0.3164m3/s      V4 = 10.4m/s

BS 8490:2007

Downpipe min velocity = 2.2m/s

Horizontal pipe min velocity = 1.0m/s

Recommended min diameter to prevent blockages = 44mm

Roughness value: Kp = 0.15mm

If 8.4m head loss assumed for P1

First Iteration: if = 1.4780

Inserting new if each iteration

(4 iterations): if = 1,722

Checking headloss due to friction

∆hf -1.722 x 8.4 = 14.46            no good so increase in diameter

------------------------------------------------------------------------------------------------------------------------

P1:  d1 = 60mm     X-SA = 0.002827m2      L1 = 8.4m    Q1 = 0.01582m3/s    V1 = 5.596m/s

Use of Colebrook-White resistance equation as above

(4 iterations): if = 0.3868

∆hf = 0.3868 x 8.4 = 3.249  passed

P2:  “

P3:  ∆hf = 5.879

P3∆hf + P1∆hf = 9.128 > 8.4    no good

------------------------------------------------------------------------------------------------------------------------

P1:  d1 = 0.07m     X-SA = 0.003848m2      L1 = 8.4m    Q1 = 0.01582m3/s    V1 = 4.111m/s

If = 0.1843 (4 iterations)       ∆hf = 0.1843 x 8.4 = 1.5478

P2:  “

P3:  d1 = 0.07m     X-SA = 0.003848m2      L1 = 15.2m    Q1 = 0.01582m3/s    V1 = 4.111m/s

If = 0.1843 (4 iterations)       ∆hf = 0.1843 x 15.2 = 1.5478

P4: d1 = 0.099m     X-SA = 0.007698m2      L1 = 13.1m    Q3 = 0.03264m3/s    V1 = 4.111m/s

If = 0.1220 (4 iterations)        ∆hf = 0.1220 x 13.1 = 1.5983

Total ∆hf  = 1.5983 + 2.8014 + 2 x 1.5478 = 7.4953m

Allowance for fittings: 1.4 x 7.4953 = 10.4933m

Velocity at point of discharge = 4.111

Velocity head Hv = 4.11122×9.81 = 0.8614

Check if HA > HT + HV        21.5m > 0.8614+10.4933 = 11.3547  passed

Minimum head pressure (hm)

Hm = 7.4953 – 0.99 = 6.5053

6.5053m > -7.8m   no risk of cavitation

------------------------------------------------------------------------------------------------------------------------

Priming time       BS 8490:2007     <60s

TF = VPQin             VP = Volume of pipework        Qin = capacity of tailpipe before primed

Qin = 4.5l/s   (EN 12056-3: 2000)

P1 Volume = 0.03232m3

P2 Volume = 0.03232m3

P3 Volume = 0.05849m3

P4 Volume = 0.1008m3

TF + 2244.5 = 50s

Gutter required to hold 50s x 31.64l/s/m2 = 1582l

Total length of gutters = 63.2m

Required XS-A gutter = 25,031mm2

Wing Siphonic Drainage calcs

A=354m2

HA=21.5m

Q0=9.589 x 1.1 = 10.548l/s

Using Colebrooke-white equation as above for siphonic drainage design

P1:  d1 = 0.044m     X-SA = 0.001521m2      L1 = 8.4m    Q1 = 0.005274m3/s    V1 = 3.4675m/s

If = 0.2353m (4 iterations)       ∆hf = 0.2353 x 8.4 = 1.9765

P2:  “

P3:  d1 = 0.044m     X-SA = 0.001521m2      L1 = 12m    Q1 = 0.005274m3/s    V1 = 3.4675m/s

If = 0.2353 (4 iterations)       ∆hf = 0.2353 x 12 = 2.8220

P4: d1 = 0.062m     X-SA = 0.003042m2      L1 = 13.1m    Q3 = 0.010548m3/s    V1 = 3.4675m/s

If = 0.1567 (4 iterations)        ∆hf = 0.1567 x 13.1 = 2.0518

HT = 2.0518 + 2.8220 + 2 x 1.9765 = 8.8268m

To allow for fittings: 1.4 x 8.8268 = 12.3575m

Velocity (u) at point of discharge = 3.4675m/s

Velocity head HV = 3.47522×9.81=0.6128

Check if HA > HT + HV

21.6 > 0.6128 + 12.3575 = 12.9703m passed

Priming time: TF = VPQin

841.5 = 56s < 60s passed

P1 Volume = 0.01278m3

P2 Volume = 0.01278m3

P3 Volume = 0.01825m3

P4 Volume = 0.03985m3

Total vol = 0.08366m3 -> 84l

Gutter needs to hold 84l

Gutter requires a 24612mm2 cross-section